Operational Status

- Last Backwash Date and Water Color	 	Unknown

- Flow Meter 1 Reading (bleed if needed)		0 no water present

- Flow Meter 2 Reading (bleed if needed)		0 no water present

- In-Fluent Pressure Tank A Reading 		0 not connected

- Effluent Pressure Tank A Reading 		0 not connected

- In-Fluent Pressure Tank B Reading 		unknown

- Effluent Pressure Tank B Reading 		unknown

- Electronic Units Status & Readings		unknown

- Pump Strainer Water Level (air / no air)		air present

- Pump Strainer Clear Of Leaves & Obstructions (yes / no)		clear

- Pump Sound (normal / not normal)		noisy – bad bearing

- Cavitation Sound (yes / no)			yes cavitation sound

Maintenance Condition

- Sand Install Date Tag Legible		Date: 	unknown – no tag

- Pump Install Date Tag Legible		Date: 	unknown – no tag

- Electronics Install Date Tag Legible	Date: 	unknown – no tag

- Pump Room Instructions Present 	 		No

- Instructions Complete & Legible 			No instructions

- All Meters Labeled & Working			No, No Labels

- All Valves Labeled & Working	 		unknown, No Labels

- Power Panel Labeled & Working			unknown, No Labels

- Electronic Panel Labeled & Working		unknown, No Labels

- Chlorinator Labeled & Working	 		unknown, No Labels

Comments

When the pump is turned off there are multiple water leaks including from the pump strainer clear top.

The pump room failed inspection. Corrective action is needed immediately, see check list and comments for specific actions.